## Sheet1
Each Panel (Meter Board) is a Slave Device; Modbus Addresses: 0 - 255
Each Slave Device: data is addressed from 0 to 65535
Design for 255 circuits. Circuit Configuration uses Holding Registers (R/W) Measurements use Input Registers (R) Each Register type has its own address space : 0 – 65535
Interpreting Register Values
Reading | Actual Value |  | Units | Size (16 bit words) | Signed?
Active Energy | Register Value * CT Rating |  | Wh | 2 | N
Active Power | Register Value * CT Rating |  | mW | 2 | N
Reactive Power | Register Value * CT Rating |  | mvar | 2 | Y
Apparent Power | Register Value * CT Rating |  | mVA | 2 | N
Power Factor | Register Value * 0.01 |  |  | 1 | N
Displacement Power Factor | Register Value * 0.01 |  |  | 1 | N
Phase Angle | Register Value |  | Degrees | 1 | Y
RMS Currents, Neutral Currents, P.E.Currents | Register Value * CT Rating |  | mA | 1 | N
Frequency | Register Value * 0.1 |  | Hz | 1 | N
L-L Voltages, L-N Voltages | Register Value * 10 |  | V | 1 | N
Active Energy (absolute) | Register Value |  | Wh | 4 | N
Active Power (absolute) | Register Value |  | mW | 2 | N
Reactive Power (absolute) | Register Value |  | mvar | 2 | Y
Apparent Power (absolute) | Register Value |  | mVA | 2 | N
Current (absolute) | Register Value |  | mA | 2 | N
When 32 bits (2 registers) are used, the first register(lower memory address) holds the most significant 16 bits and the second register (higher memory address) holds the least significant 16 bits.
Reactive Power and Phase angle are signed quantities using two's complement notation.
Holding Registers (R/W) Used for Circuit Configuration
Address (HEX) | Offset | Description | Notes | Size (16 bit words) | Access Level
0010 |  | Panel/Power Meter Configuration
| 0 | Meter Class: 1: Power Meter 2: Panel |  | 1 | R
| 1 | Meter Board ID |  | 1 | R
| 2 | Number of Circuit Positions |  | 1 | R
| 3 | Panel Layout: 1: One Column 2: Two Columns |  | 1 | R
| 4 | Panel Numbering: Odd/Even 0: Sequential 1: Odd/Even |  | 1 | R
| 5 | Mains CT Rating: 0 indicates CT is disabled |  | 1 | R
| 6 | Neutral CT Rating: 0 indicates CT is disabled |  | 1 | R
| 7 | P.E. CT Rating: 0 indicates CT is disabled |  | 1 | R
| 8 | Panel Breaker Rating |  | 1 | R
| 9 | Meter Type: 1: single-phase 2: split-phase 3; 3-phase |  | 1 | R
0020 |  | Circuit Position Phases |  |  | R
| 0 | Mains A | Always A | 1 | R
| 1 | Mains B | used only if Meter Type is split-phase or 3-phase | 1 | R
| 2 | Mains C | used only if Meter Type is split-phase or 3-phase | 1 | R
| 3 | Circuit Position 1 Phase: 1: A, 2: B, 3:C |  | 1 | R
| 4 | Circuit Position 2 Phase: 1: A, 2: B, 3:C |  | 1 | R
|  | ... |  |  | R
| 3 + c-1 | Circuit Position c Phase: 1: A, 2: B, 3:C |  | 1 | R
…
0120 |  | Circuit Position CT Numbers |  |  | R
| 0 | CT # connected to Mains A | Unused, always 0 |  | R
| 1 | CT # connected to Mains B | Unused, always 0 |  | R
| 2 | CT # connected to Mains C | Unused, always 0 |  | R
| 3 | CT # connected to Circuit Position 1 |  | 1 | R
| 4 | CT # connected to Circuit Position 2 |  | 1 | R
|  | ... |  |  | R
| 3 + c-1 | CT # connected to Circuit Position c |  | 1 | R
…
0220 |  | Circuit Breaker Ratings |  |  | R
| 0 | Panel Breaker rating |  | 1 | R
| 1 | Circuit 1 Breaker Rating |  | 1 | R
|  | ... |  |  | R
| c | Circuit c Breaker Rating |  | 1 | R
…
0320 |  | Circuit CT Ratings |  |  | R
| 0 | Mains CT rating: 0 indicates CT is disabled |  | 1 | R
| 1 | Neutral CT Rating: 0 indicates CT is disabled |  | 1 | R
| 2 | P.E. CT Rating: 0 indicates CT is disabled |  | 1 | R
| 3 | Circuit 1 CT Rating |  | 1 | R
|  | ... |  |  | R
| 3 + c-1 | Circuit c CT Rating |  | 1 | R
…
0420 |  | Circuit Types |  |  | R
| 0 | Mains Circuit Type: Depends on meter type as shown below. Meter Type Circuit Type 3-phase: 4(3-phase) split-phase: 3(1-phase L-L-N) single-phase: 1 (L-N) |  |  | R
| 1 | Circuit 1 Circuit Type: 0: None, 1: 1-phase L-N, 2: 1-phase L-L, 3: 1-phase L-L-N, 4: 3-phase |  | 1 | R
|  | ... |  |  | R
| c | Circuit c Circuit Type |  | 1 | R
…
Recommended Procedure for Changing Thresholds 1) Disable all Thresholds 2) Set values of thresholds, assertion delays and hysteresis 3) Enable the thresholds
0520 |  | Frequency: Circuit Position Thresholds
Enabled Thresholds Bit 0: Upper Critical Bit 1: Upper Warning Bit 2: Lower Warning Bit 3: Lower Critical
| 0 | Mains |  | 1 | R/W
|  | ... |  |  | R/W
0620 |  | Upper Critical Thresholds
| 0 | Mains |  | 1 | R/W
|  | ... |  |  | R/W
0720 |  | Upper Warning Thresholds
| 0 | Mains |  | 1 | R/W
|  | ... |  |  | R/W
0820 |  | Lower Warning Thresholds
| 0 | Mains |  | 1 | R/W
|  | ... |  |  | R/W
0920 |  | Lower Critical Thresholds
| 0 | Mains |  | 1 | R/W
|  | ... |  |  | R/W
0A20 |  | Hysteresis
| 0 | Hysteresis |  | 1 | R/W
|  | ... |  |  | R/W
0B20 |  | Assertion Delays
| 0 | Assertion Delays |  | 1 | R/W
|  | ... |  |  | R/W
0C20 |  | LineToLine Voltage: Circuit Position Thresholds
Enabled Thresholds Bit 0: Upper Critical Bit 1: Upper Warning Bit 2: Lower Warning Bit 3: Lower Critical
| 0 | a-b |  | 1 | R/W
| 1 | b-c |  | 1 | R/W
| 2 | c-a |  | 1 | R/W
|  | ... |  |  | R/W
0D20 |  | Upper Critical Thresholds
| 0 | a-b |  | 1 | R/W
| 1 | b-c |  | 1 | R/W
| 2 | c-a |  | 1 | R/W
|  | ... |  |  | R/W
0E20 |  | Upper Warning Thresholds
| 0 | a-b |  | 1 | R/W
| 1 | b-c |  | 1 | R/W
| 2 | c-a |  | 1 | R/W
|  | ... |  |  | R/W
0F20 |  | Lower Warning Thresholds
| 0 | a-b |  | 1 | R/W
| 1 | b-c |  | 1 | R/W
| 2 | c-a |  | 1 | R/W
|  | ... |  |  | R/W
1020 |  | Lower Critical Thresholds
| 0 | a-b |  | 1 | R/W
| 1 | b-c |  | 1 | R/W
| 2 | c-a |  | 1 | R/W
|  | ... |  |  | R/W
1120 |  | Hysteresis
| 0 | a-b |  | 1 | R/W
| 1 | b-c |  | 1 | R/W
| 2 | c-a |  | 1 | R/W
|  | ... |  |  | R/W
1220 |  | Assertion Delays
| 0 | a-b |  | 1 | R/W
| 1 | b-c |  | 1 | R/W
| 2 | c-a |  | 1 | R/W
|  | ... |  |  | R/W
1320 |  | LineToNeutral Voltage: Circuit Position Thresholds
Enabled Thresholds Bit 0: Upper Critical Bit 1: Upper Warning Bit 2: Lower Warning Bit 3: Lower Critical
| 0 | a-n |  | 1 | R/W
| 1 | b-n |  | 1 | R/W
| 1 | c-n |  | 1 | R/W
|  | ... |  |  | R/W
1420 |  | Upper Critical Thresholds
| 0 | a-n |  | 1 | R/W
| 1 | b-n |  | 1 | R/W
| 1 | c-n |  | 1 | R/W
|  | ... |  |  | R/W
1520 |  | Upper Warning Thresholds
| 0 | a-n |  | 1 | R/W
| 1 | b-n |  | 1 | R/W
| 1 | c-n |  | 1 | R/W
|  | ... |  |  | R/W
1620 |  | Lower Warning Thresholds
| 0 | a-n |  | 1 | R/W
| 1 | b-n |  | 1 | R/W
| 1 | c-n |  | 1 | R/W
|  | ... |  |  | R/W
1720 |  | Lower Critical Thresholds
| 0 | a-n |  | 1 | R/W
| 1 | b-n |  | 1 | R/W
| 1 | c-n |  | 1 | R/W
|  | ... |  |  | R/W
1820 |  | Hysteresis
| 0 | a-n |  | 1 | R/W
| 1 | b-n |  | 1 | R/W
| 2 | c-n |  | 1 | R/W
|  | ... |  |  | R/W
1920 |  | Assertion Delays
| 0 | a-n |  | 1 | R/W
| 1 | b-n |  | 1 | R/W
| 2 | c-n |  | 1 | R/W
|  | ... |  |  | R/W
1A20 | Active Energy: Circuit Summary Thresholds
Enabled Thresholds Bit 0: Upper Critical Bit 1: Upper Warning Bit 2: Lower Warning Bit 3: Lower Critical
| 0 | Mains |  | 1 | R/W
| 1 | Circuit 1 |  | 1 | R/W
|  | ... |  |  | R/W
| c | Circuit c |  | 1 | R/W
|  | ... |  |  | R/W
1B20 |  | Upper Critical Thresholds
| 0 | Mains |  | 2 | R/W
| 2 | Circuit 1 |  | 2 | R/W
|  | ... |  |  | R/W
| 2c | Circuit c |  | 2 | R/W
|  | ... |  |  | R/W
1D20 |  | Upper Warning Thresholds
| 0 | Mains |  | 2 | R/W
| 2 | Circuit 1 |  | 2 | R/W
|  | ... |  |  | R/W
| 2c | Circuit c |  | 2 | R/W
|  | ... |  |  | R/W
1F20 |  | Lower Warning Thresholds
| 0 | Mains |  | 2 | R/W
| 2 | Circuit 1 |  | 2 | R/W
|  | ... |  |  | R/W
| 2c | Circuit c |  | 2 | R/W
|  | ... |  |  | R/W
2120 |  | Lower Critical Thresholds
| 0 | Mains |  | 2 | R/W
| 2 | Circuit 1 |  | 2 | R/W
|  | ... |  |  | R/W
| 2c | Circuit c |  | 2 | R/W
|  | ... |  |  | R/W
2320 |  | Hysteresis
| 0 | Mains |  | 2 | R/W
| 2 | Circuit 1 |  | 2 | R/W
|  | ... |  |  | R/W
| 2c | Circuit c |  | 2 | R/W
|  | ... |  |  | R/W
2520 |  | Assertion Delays
| 0 | Mains |  | 1 | R/W
| 1 | Circuit 1 |  | 1 | R/W
|  | ... |  |  | R/W
| c | Circuit c |  | 1 | R/W
|  | ... |  |  | R/W
2620 | Active Power: Circuit Summary Thresholds
Enabled Thresholds Bit 0: Upper Critical Bit 1: Upper Warning Bit 2: Lower Warning Bit 3: Lower Critical
| 0 | Mains |  | 1 | R/W
| 1 | Circuit 1 |  | 1 | R/W
|  | ... |  |  | R/W
| c | Circuit c |  | 1 | R/W
|  | ... |  |  | R/W
2720 |  | Upper Critical Thresholds
| 0 | Mains |  | 2 | R/W
| 2 | Circuit 1 |  | 2 | R/W
|  | ... |  |  | R/W
| 2c | Circuit c |  | 2 | R/W
|  | ... |  |  | R/W
2920 |  | Upper Warning Thresholds
| 0 | Mains |  | 2 | R/W
| 2 | Circuit 1 |  | 2 | R/W
|  | ... |  |  | R/W
| 2c | Circuit c |  | 2 | R/W
|  | ... |  |  | R/W
2B20 |  | Lower Warning Thresholds
| 0 | Mains |  | 2 | R/W
| 2 | Circuit 1 |  | 2 | R/W
|  | ... |  |  | R/W
| 2c | Circuit c |  | 2 | R/W
|  | ... |  |  | R/W
2D20 |  | Lower Critical Thresholds
| 0 | Mains |  | 2 | R/W
| 2 | Circuit 1 |  | 2 | R/W
|  | ... |  |  | R/W
| 2c | Circuit c |  | 2 | R/W
|  | ... |  |  | R/W
2F20 |  | Hysteresis
| 0 | Mains |  | 2 | R/W
| 2 | Circuit 1 |  | 2 | R/W
|  | ... |  |  | R/W
| 2c | Circuit c |  | 2 | R/W
|  | ... |  |  | R/W
3120 |  | Assertion Delays
| 0 | Mains |  | 1 | R/W
| 1 | Circuit 1 |  | 1 | R/W
|  | ... |  |  | R/W
| c | Circuit c |  | 1 | R/W
|  | ... |  |  | R/W
3220 | Reactive Power: Circuit Summary Thresholds
Enabled Thresholds Bit 0: Upper Critical Bit 1: Upper Warning Bit 2: Lower Warning Bit 3: Lower Critical
| 0 | Mains |  | 1 | R/W
| 1 | Circuit 1 |  | 1 | R/W
|  | ... |  |  | R/W
| c | Circuit c |  | 1 | R/W
|  | ... |  |  | R/W
3320 |  | Upper Critical Thresholds
| 0 | Mains |  | 2 | R/W
| 2 | Circuit 1 |  | 2 | R/W
|  | ... |  |  | R/W
| 2c | Circuit c |  | 2 | R/W
|  | ... |  |  | R/W
3520 |  | Upper Warning Thresholds
| 0 | Mains |  | 2 | R/W
| 2 | Circuit 1 |  | 2 | R/W
|  | ... |  |  | R/W
| 2c | Circuit c |  | 2 | R/W
|  | ... |  |  | R/W
3720 |  | Lower Warning Thresholds
| 0 | Mains |  | 2 | R/W
| 2 | Circuit 1 |  | 2 | R/W
|  | ... |  |  | R/W
| 2c | Circuit c |  | 2 | R/W
|  | ... |  |  | R/W
3920 |  | Lower Critical Thresholds
| 0 | Mains |  | 2 | R/W
| 2 | Circuit 1 |  | 2 | R/W
|  | ... |  |  | R/W
| 2c | Circuit c |  | 2 | R/W
|  | ... |  |  | R/W
3B20 |  | Hysteresis
| 0 | Mains |  | 2 | R/W
| 2 | Circuit 1 |  | 2 | R/W
|  | ... |  |  | R/W
| 2c | Circuit c |  | 2 | R/W
|  | ... |  |  | R/W
3D20 |  | Assertion Delays
| 0 | Mains |  | 1 | R/W
| 1 | Circuit 1 |  | 1 | R/W
|  | ... |  |  | R/W
| c | Circuit c |  | 1 | R/W
|  | ... |  |  | R/W
3E20 | Apparent Power: Circuit Position Thresholds
Enabled Thresholds Bit 0: Upper Critical Bit 1: Upper Warning Bit 2: Lower Warning Bit 3: Lower Critical
| 0 | a |  | 1 | R/W
| 1 | b |  | 1 | R/W
| 2 | c |  | 1 | R/W
| 3 | Circuit Position 1 |  | 1 | R/W
|  | ... |  | 1 | R/W
| 3+(c-1) | Circuit Position c |  | 1 | R/W
|  | ... |  | 1 | R/W
3F20 |  | Upper Critical Thresholds
| 0 | a |  | 2 | R/W
| 2 | b |  | 2 | R/W
| 4 | c |  | 2 | R/W
| 6 | Circuit Position 1 |  | 2 | R/W
|  | ... |  | 2 | R/W
| 6+(c-1)*2 | Circuit Position c |  | 2 | R/W
|  | ... |  | 2 | R/W
4120 |  | Upper Warning Thresholds
| 0 | a |  | 2 | R/W
| 2 | b |  | 2 | R/W
| 4 | c |  | 2 | R/W
| 6 | Circuit Position 1 |  | 2 | R/W
|  | ... |  | 2 | R/W
| 6+(c-1)*2 | Circuit Position c |  | 2 | R/W
|  | ... |  | 2 | R/W
4320 |  | Lower Warning Thresholds
| 0 | a |  | 2 | R/W
| 2 | b |  | 2 | R/W
| 4 | c |  | 2 | R/W
| 6 | Circuit Position 1 |  | 2 | R/W
|  | ... |  | 2 | R/W
| 6+(c-1)*2 | Circuit Position c |  | 2 | R/W
|  | ... |  | 2 | R/W
4520 |  | Lower Critical Thresholds
| 0 | a |  | 2 | R/W
| 2 | b |  | 2 | R/W
| 4 | c |  | 2 | R/W
| 6 | Circuit Position 1 |  | 2 | R/W
|  | ... |  | 2 | R/W
| 6+(c-1)*2 | Circuit Position c |  | 2 | R/W
|  | ... |  | 2 | R/W
4720 |  | Hysteresis
| 0 | a |  | 2 | R/W
| 2 | b |  | 2 | R/W
| 4 | c |  | 2 | R/W
| 6 | Circuit Position 1 |  | 2 | R/W
|  | ... |  | 2 | R/W
| 6+(c-1)*2 | Circuit Position c |  | 2 | R/W
|  | ... |  | 2 | R/W
4920 |  | Assertion Delays
| 0 | a |  | 1 | R/W
| 1 | b |  | 1 | R/W
| 2 | c |  | 1 | R/W
| 3 | Circuit Position 1 |  | 1 | R/W
|  | ... |  | 1 | R/W
| 3+(c-1) | Circuit Position c |  | 1 | R/W
|  | ... |  | 1 | R/W
4A20 | Power Factor: Circuit Position Thresholds
Enabled Thresholds Bit 0: Upper Critical Bit 1: Upper Warning Bit 2: Lower Warning Bit 3: Lower Critical
| 0 | a |  | 1 | R/W
| 1 | b |  | 1 | R/W
| 2 | c |  | 1 | R/W
| 3 | Circuit Position 1 |  | 1 | R/W
|  | ... |  | 1 | R/W
| 3+(c-1) | Circuit Position c |  | 1 | R/W
|  | ... |  | 1 | R/W
4B20 |  | Upper Critical Thresholds
| 0 | a |  | 1 | R/W
| 1 | b |  | 1 | R/W
| 2 | c |  | 1 | R/W
| 3 | Circuit Position 1 |  | 1 | R/W
|  | ... |  | 1 | R/W
| 3+(c-1) | Circuit Position c |  | 1 | R/W
|  | ... |  | 1 | R/W
4C20 |  | Upper Warning Thresholds
| 0 | a |  | 1 | R/W
| 1 | b |  | 1 | R/W
| 2 | c |  | 1 | R/W
| 3 | Circuit Position 1 |  | 1 | R/W
|  | ... |  | 1 | R/W
| 3 + (c-1) | Circuit Position c |  | 1 | R/W
|  | ... |  | 1 | R/W
4D20 |  | Lower Warning Thresholds |  | 1
| 0 | a |  | 1 | R/W
| 1 | b |  | 1 | R/W
| 2 | c |  | 1 | R/W
| 3 | Circuit Position 1 |  | 1 | R/W
|  | ... |  | 1 | R/W
| 3+ (c-1) | Circuit Position c |  | 1 | R/W
|  | ... |  | 1 | R/W
4E20 |  | Lower Critical Thresholds |  | 1
| 0 | a |  | 1 | R/W
| 1 | b |  | 1 | R/W
| 2 | c |  | 1 | R/W
| 3 | Circuit Position 1 |  | 1 | R/W
|  | ... |  | 1 | R/W
| 3+(c-1) | Circuit Position c |  | 1 | R/W
|  | ... |  | 1 | R/W
4F20 |  | Hysteresis |  | 1
| 0 | a |  | 1 | R/W
| 1 | b |  | 1 | R/W
| 2 | c |  | 1 | R/W
| 3 | Circuit Position 1 |  | 1 | R/W
|  | ... |  | 1 | R/W
| 3 + (c-1) | Circuit Position c |  | 1 | R/W
|  | ... |  | 1 | R/W
5020 |  | Assertion Delays |  | 1
| 0 | a |  | 1 | R/W
| 1 | b |  | 1 | R/W
| 2 | c |  | 1 | R/W
| 3 | Circuit Position 1 |  | 1 | R/W
|  | ... |  | 1 | R/W
| 3+(c-1) | Circuit Position c |  | 1 | R/W
|  | ... |  | 1 | R/W
5120 | Displacement Power Factor: Circuit Position Thresholds
Enabled Thresholds Bit 0: Upper Critical Bit 1: Upper Warning Bit 2: Lower Warning Bit 3: Lower Critical
| 0 | a |  | 1 | R/W
| 1 | b |  | 1 | R/W
| 2 | c |  | 1 | R/W
| 3 | Circuit Position 1 |  | 1 | R/W
|  | ... |  | 1 | R/W
| 3+(c-1) | Circuit Position c |  | 1 | R/W
|  | ... |  | 1 | R/W
5220 |  | Upper Critical Thresholds
| 0 | a |  | 1 | R/W
| 1 | b |  | 1 | R/W
| 2 | c |  | 1 | R/W
| 3 | Circuit Position 1 |  | 1 | R/W
|  | ... |  | 1 | R/W
| 3+(c-1) | Circuit Position c |  | 1 | R/W
|  | ... |  | 1 | R/W
5320 |  | Upper Warning Thresholds
| 0 | a |  | 1 | R/W
| 1 | b |  | 1 | R/W
| 2 | c |  | 1 | R/W
| 3 | Circuit Position 1 |  | 1 | R/W
|  | ... |  | 1 | R/W
| 3 + (c-1) | Circuit Position c |  | 1 | R/W
|  | ... |  | 1 | R/W
5420 |  | Lower Warning Thresholds |  | 1
| 0 | a |  | 1 | R/W
| 1 | b |  | 1 | R/W
| 2 | c |  | 1 | R/W
| 3 | Circuit Position 1 |  | 1 | R/W
|  | ... |  | 1 | R/W
| 3+ (c-1) | Circuit Position c |  | 1 | R/W
|  | ... |  | 1 | R/W
5520 |  | Lower Critical Thresholds |  | 1
| 0 | a |  | 1 | R/W
| 1 | b |  | 1 | R/W
| 2 | c |  | 1 | R/W
| 3 | Circuit Position 1 |  | 1 | R/W
|  | ... |  | 1 | R/W
| 3+(c-1) | Circuit Position c |  | 1 | R/W
|  | ... |  | 1 | R/W
5620 |  | Hysteresis |  | 1
| 0 | a |  | 1 | R/W
| 1 | b |  | 1 | R/W
| 2 | c |  | 1 | R/W
| 3 | Circuit Position 1 |  | 1 | R/W
|  | ... |  | 1 | R/W
| 3 + (c-1) | Circuit Position c |  | 1 | R/W
|  | ... |  | 1 | R/W
5720 |  | Assertion Delays |  | 1
| 0 | a |  | 1 | R/W
| 1 | b |  | 1 | R/W
| 2 | c |  | 1 | R/W
| 3 | Circuit Position 1 |  | 1 | R/W
|  | ... |  | 1 | R/W
| 3+(c-1) | Circuit Position c |  | 1 | R/W
|  | ... |  | 1 | R/W
5820 | Phase Angle Circuit Position Thresholds
Enabled Thresholds Bit 0: Upper Critical Bit 1: Upper Warning Bit 2: Lower Warning Bit 3: Lower Critical
| 0 | a |  | 1 | R/W
| 1 | b |  | 1 | R/W
| 2 | c |  | 1 | R/W
| 3 | Circuit Position 1 |  | 1 | R/W
|  | ... |  | 1 | R/W
| 3+(c-1) | Circuit Position c |  | 1 | R/W
|  | ... |  | 1 | R/W
5920 |  | Upper Critical Thresholds
| 0 | a |  | 1 | R/W
| 1 | b |  | 1 | R/W
| 2 | c |  | 1 | R/W
| 3 | Circuit Position 1 |  | 1 | R/W
|  | ... |  | 1 | R/W
| 3+(c-1) | Circuit Position c |  | 1 | R/W
|  | ... |  | 1 | R/W
5A20 |  | Upper Warning Thresholds
| 0 | a |  | 1 | R/W
| 1 | b |  | 1 | R/W
| 2 | c |  | 1 | R/W
| 3 | Circuit Position 1 |  | 1 | R/W
|  | ... |  | 1 | R/W
| 3 + (c-1) | Circuit Position c |  | 1 | R/W
|  | ... |  | 1 | R/W
5B20 |  | Lower Warning Thresholds |  | 1
| 0 | a |  | 1 | R/W
| 1 | b |  | 1 | R/W
| 2 | c |  | 1 | R/W
| 3 | Circuit Position 1 |  | 1 | R/W
|  | ... |  | 1 | R/W
| 3+ (c-1) | Circuit Position c |  | 1 | R/W
|  | ... |  | 1 | R/W
5C20 |  | Lower Critical Thresholds |  | 1
| 0 | a |  | 1 | R/W
| 1 | b |  | 1 | R/W
| 2 | c |  | 1 | R/W
| 3 | Circuit Position 1 |  | 1 | R/W
|  | ... |  | 1 | R/W
| 3+(c-1) | Circuit Position c |  | 1 | R/W
|  | ... |  | 1 | R/W
5D20 |  | Hysteresis |  | 1
| 0 | a |  | 1 | R/W
| 1 | b |  | 1 | R/W
| 2 | c |  | 1 | R/W
| 3 | Circuit Position 1 |  | 1 | R/W
|  | ... |  | 1 | R/W
| 3 + (c-1) | Circuit Position c |  | 1 | R/W
|  | ... |  | 1 | R/W
5E20 |  | Assertion Delays |  | 1
| 0 | a |  | 1 | R/W
| 1 | b |  | 1 | R/W
| 2 | c |  | 1 | R/W
| 3 | Circuit Position 1 |  | 1 | R/W
|  | ... |  | 1 | R/W
| 3+(c-1) | Circuit Position c |  | 1 | R/W
|  | ... |  | 1 | R/W
5F20 | RMS Current: Circuit Summary Thresholds
Enabled Thresholds Bit 0: Upper Critical Bit 1: Upper Warning Bit 2: Lower Warning Bit 3: Lower Critical
| 0 | Mains |  | 1 | R/W
| 1 | Circuit 1 |  | 1 | R/W
|  | ... |  |  | R/W
| c | Circuit c |  | 1 | R/W
|  | ... |  |  | R/W
6020 |  | Upper Critical Thresholds
| 0 | Mains |  | 1 | R/W
| 1 | Circuit 1 |  | 1 | R/W
|  | ... |  | 1 | R/W
| c | Circuit c |  | 1 | R/W
|  | ... |  | 1 | R/W
6120 |  | Upper Warning Thresholds |  | 1
| 0 | Mains |  | 1 | R/W
| 1 | Circuit 1 |  | 1 | R/W
|  | ... |  | 1 | R/W
| c | Circuit c |  | 1 | R/W
|  | ... |  | 1 | R/W
6220 |  | Lower Warning Thresholds |  | 1
| 0 | Mains |  | 1 | R/W
| 1 | Circuit 1 |  | 1 | R/W
|  | ... |  | 1 | R/W
| c | Circuit c |  | 1 | R/W
|  | ... |  | 1 | R/W
6320 |  | Lower Critical Thresholds |  | 1
| 0 | Mains |  | 1 | R/W
| 1 | Circuit 1 |  | 1 | R/W
|  | ... |  | 1 | R/W
| c | Circuit c |  | 1 | R/W
|  | ... |  | 1 | R/W
6420 |  | Hysteresis |  | 1
| 0 | Mains |  | 1 | R/W
| 1 | Circuit 1 |  | 1 | R/W
|  | ... |  | 1 | R/W
| c | Circuit c |  | 1 | R/W
|  | ... |  | 1 | R/W
6520 |  | Assertion Delays
| 0 | Mains |  | 1 | R/W
| 1 | Circuit 1 |  | 1 | R/W
|  | ... |  |  | R/W
| c | Circuit c |  | 1 | R/W
|  | ... |  |  | R/W
6620 |  | Neutral Currents: Circuit Position Thresholds
Enabled Thresholds Bit 0: Upper Critical Bit 1: Upper Warning Bit 2: Lower Warning Bit 3: Lower Critical
| 0 | Neutral Current |  | 1 | R/W
|  | ... |  |  | R/W
6720 |  | Upper Critical Thresholds
| 0 | Neutral Current |  | 1 | R/W
|  | ... |  |  | R/W
6820 |  | Upper Warning Thresholds
| 0 | Neutral Current |  | 1 | R/W
|  | ... |  |  | R/W
6920 |  | Lower Warning Thresholds
| 0 | Neutral Current |  | 1 | R/W
|  | ... |  |  | R/W
6A20 |  | Lower Critical Thresholds
| 0 | Neutral Current |  | 1 | R/W
|  | ... |  |  | R/W
6B20 |  | Hysteresis
| 0 | Neutral Current |  | 1 | R/W
|  | ... |  |  | R/W
6C20 |  | Assertion Delays
| 0 | Neutral Current |  | 1 | R/W
|  | ... |  |  | R/W
6D20 |  | P.E. Currents: Circuit Position Thresholds
Enabled Thresholds Bit 0: Upper Critical Bit 1: Upper Warning Bit 2: Lower Warning Bit 3: Lower Critical
| 0 | P.E Current |  | 1 | R/W
|  | ... |  |  | R/W
6E20 |  | Upper Critical Thresholds
| 0 | P.E Current |  | 1 | R/W
|  | ... |  |  | R/W
6F20 |  | Upper Warning Thresholds
| 0 | P.E Current |  | 1 | R/W
|  | ... |  |  | R/W
7020 |  | Lower Warning Thresholds
| 0 | P.E Current |  | 1 | R/W
|  | ... |  |  | R/W
7120 |  | Lower Critical Thresholds
| 0 | P.E Current |  | 1 | R/W
|  | ... |  |  | R/W
7220 |  | Hysteresis
| 0 | P.E Current |  | 1 | R/W
|  | ... |  |  | R/W
7320 |  | Assertion Delays
| 0 | P.E Current |  | 1 | R/W
|  | ... |  |  | R/W
Input Registers (R) Used for Measurements
Address (HEX) | Offset | Description | Notes | Size (16 bit words)
Frequency
0010 |  | Circuit Positions
| 0 | Frequency |  | 1 | R
|  | … |  |  | R
0110 |  | Circuit Position Events
| 0 | Upper Critical 1 |  | 1 | R
|  | … |  |  | R
| 15 | Upper Critical 16 |  | 1 | R
| 16 | Upper Warning 1 |  | 1 | R
|  | … |  |  | R
| 31 | Upper Warning 16 |  | 1 | R
| 32 | Lower Warning 1 |  | 1 | R
|  | … |  |  | R
| 47 | Lower Warning 16 |  | 1 | R
| 48 | Lower Critical 1 |  | 1 | R
|  | … |  |  | R
| 63 | Lower Critical 16 |  | 1 | R
L-L Voltages
0150 |  | Circuit Positions
| 0 | A L-L |  | 1 | R
| 1 | B L-L |  | 1 | R
| 2 | C L-L |  | 1 | R
|  | … |  |  | R
0250 |  | Circuit Position Events
| 0 | Upper Critical 1 |  | 1 | R
|  | … |  |  | R
| 15 | Upper Critical 16 |  | 1 | R
| 16 | Upper Warning 1 |  | 1 | R
|  | … |  |  | R
| 31 | Upper Warning 16 |  | 1 | R
| 32 | Lower Warning 1 |  | 1 | R
|  | … |  |  | R
| 47 | Lower Warning 16 |  | 1 | R
| 48 | Lower Critical 1 |  | 1 | R
|  | … |  |  | R
| 63 | Lower Critical 16 |  | 1 | R
L-N Voltages
0290 |  | Circuit Positions
| 0 | A L-N |  | 1 | R
| 1 | B L-N |  | 1 | R
| 2 | C L-N |  | 1 | R
|  | … |  |  | R
0390 |  | Circuit Position Events
| 0 | Upper Critical 1 |  | 1 | R
|  | … |  |  | R
| 15 | Upper Critical 16 |  | 1 | R
| 16 | Upper Warning 1 |  | 1 | R
|  | … |  |  | R
| 31 | Upper Warning 16 |  | 1 | R
| 32 | Lower Warning 1 |  | 1 | R
|  | .. |  |  | R
| 47 | Lower Warning 16 |  | 1 | R
| 48 | Lower Critical 1 |  | 1 | R
|  | … |  |  | R
| 63 | Lower Critical 16 |  | 1 | R
Active Energy
03D0 |  | Circuit Summary Readings
| 0 | Mains |  | 2 | R
| 2 | Circuit 1 |  | 2 | R
|  | … |  |  | R
| c*2 | Circuit c |  | 2 | R
|  | … |  |  | R
05D0 |  | Circuit Summary Events
| 0 | Upper Critical 1 |  | 1 | R
|  | … |  |  | R
| 15 | Upper Critical 16 |  | 1 | R
| 16 | Upper Warning 1 |  | 1 | R
|  | … |  |  | R
| 31 | Upper Warning 16 |  | 1 | R
| 32 | Lower Warning 1 |  | 1 | R
|  | … |  |  | R
| 47 | Lower Warning 16 |  | 1 | R
| 48 | Lower Critical 1 |  | 1 | R
|  | … |  |  | R
| 63 | Lower Critical 16 |  | 1 | R
0610 |  | Circuit Position Readings
| 0 | Mains A |  | 2 | R
| 2 | Mains B |  | 2 | R
| 4 | Mains C |  | 2 | R
| 6 | Circuit Position 1 |  | 2 | R
|  | … |  |  | R
| 6 + (c-1)* 2 | Circuit Position c |  | 2 | R
|  | … |  |  | R
0810 |  | Circuit Position Events
| 0 | Upper Critical 1 |  | 1 | R
|  | … |  |  | R
| 15 | Upper Critical 16 |  | 1 | R
| 16 | Upper Warning 1 |  | 1 | R
|  | … |  |  | R
| 31 | Upper Warning 16 |  | 1 | R
| 32 | Lower Warning 1 |  | 1 | R
|  | … |  |  | R
| 47 | Lower Warning 16 |  | 1 | R
| 48 | Lower Critical 1 |  | 1 | R
|  | … |  |  | R
| 63 | Lower Critical 16 |  | 1 | R
Active Power
0850 |  | Circuit Summary Readings
| 0 | Mains |  | 2 | R
| 2 | Circuit 1 |  | 2 | R
|  | … |  |  | R
| c*2 | Circuit c |  | 2 | R
|  | … |  |  | R
0A50 |  | Circuit Summary Events
| 0 | Upper Critical 1 |  | 1 | R
|  | … |  |  | R
| 15 | Upper Critical 16 |  | 1 | R
| 16 | Upper Warning 1 |  | 1 | R
|  | … |  |  | R
| 31 | Upper Warning 16 |  | 1 | R
| 32 | Lower Warning 1 |  | 1 | R
|  | … |  |  | R
| 47 | Lower Warning 16 |  | 1 | R
| 48 | Lower Critical 1 |  | 1 | R
|  | … |  |  | R
| 63 | Lower Critical 16 |  | 1 | R
0A90 |  | Circuit Position Readings
| 0 | Mains A |  | 2 | R
| 2 | Mains B |  | 2 | R
| 4 | Mains C |  | 2 | R
| 6 | Circuit Position 1 |  | 2 | R
|  | … |  |  | R
| 6 + (c-1)* 2 | Circuit Position c |  | 2 | R
|  | … |  |  | R
0C90 |  | Circuit Position Events
| 0 | Upper Critical 1 |  | 1 | R
|  | … |  |  | R
| 15 | Upper Critical 16 |  | 1 | R
| 16 | Upper Warning 1 |  | 1 | R
|  | … |  |  | R
| 31 | Upper Warning 16 |  | 1 | R
| 32 | Lower Warning 1 |  | 1 | R
|  | … |  |  | R
| 47 | Lower Warning 16 |  | 1 | R
| 48 | Lower Critical 1 |  | 1 | R
|  | … |  |  | R
| 63 | Lower Critical 16 |  | 1 | R
Reactive Power
0CD0 |  | Circuit Summary Readings
| 0 | Mains |  | 2 | R
| 2 | Circuit 1 |  | 2 | R
|  | … |  | 2 | R
| c*2 | Circuit c |  | 2 | R
|  | … |  |  | R
0ED0 |  | Circuit Summary Events
| 0 | Upper Critical 1 |  | 1 | R
|  | … |  |  | R
| 15 | Upper Critical 16 |  | 1 | R
| 16 | Upper Warning 1 |  | 1 | R
|  | … |  |  | R
| 31 | Upper Warning 16 |  | 1 | R
| 32 | Lower Warning 1 |  | 1 | R
|  | … |  |  | R
| 47 | Lower Warning 16 |  | 1 | R
| 48 | Lower Critical 1 |  | 1 | R
|  | … |  |  | R
| 63 | Lower Critical 16 |  | 1 | R
0F10 |  | Circuit Position Readings
| 0 | Mains A |  | 2 | R
| 2 | Mains B |  | 2 | R
| 4 | Mains C |  | 2 | R
| 6 | Circuit Position 1 |  | 2 | R
|  | … |  |  | R
| 6 + (c-1)* 2 | Circuit Position c |  | 2 | R
|  | … |  |  | R
1110 |  | Circuit Position Events
| 0 | Upper Critical 1 |  | 1 | R
|  | … |  |  | R
| 15 | Upper Critical 16 |  | 1 | R
| 16 | Upper Warning 1 |  | 1 | R
|  | … |  |  | R
| 31 | Upper Warning 16 |  | 1 | R
| 32 | Lower Warning 1 |  | 1 | R
|  | … |  |  | R
| 47 | Lower Warning 16 |  | 1 | R
| 48 | Lower Critical 1 |  | 1 | R
|  | … |  |  | R
| 63 | Lower Critical 16 |  | 1 | R
Apparent Power
1150 |  | Circuit Position Readings
| 0 | Mains A |  | 2 | R
| 2 | Mains B |  | 2 | R
| 4 | Mains C |  | 2 | R
| 6 | Circuit Position 1 |  | 2 | R
|  | … |  |  | R
| 6 + (c-1)* 2 | Circuit Position c |  | 2 | R
|  | … |  |  | R
1350 |  | Circuit Position Events
| 0 | Upper Critical 1 |  | 1 | R
|  | … |  |  | R
| 15 | Upper Critical 16 |  | 1 | R
| 16 | Upper Warning 1 |  | 1 | R
|  | … |  |  | R
| 31 | Upper Warning 16 |  | 1 | R
| 32 | Lower Warning 1 |  | 1 | R
|  | … |  |  | R
| 47 | Lower Warning 16 |  | 1 | R
| 48 | Lower Critical 1 |  | 1 | R
|  | … |  |  | R
| 63 | Lower Critical 16 |  | 1 | R
Power Factor
1390 |  | Circuit Position Readings
| 0 | Mains A |  | 1 | R
| 1 | Mains B |  | 1 | R
| 2 | Mains C |  | 1 | R
| 3 | Circuit Position 1 |  | 1 | R
|  | … |  |  | R
| 3 + (c-1) | Circuit Position c |  | 1 | R
|  | … |  |  | R
1490 |  | Circuit Position Events
| 0 | Upper Critical 1 |  | 1 | R
|  | … |  |  | R
| 15 | Upper Critical 16 |  | 1 | R
| 16 | Upper Warning 1 |  | 1 | R
|  | … |  |  | R
| 31 | Upper Warning 16 |  | 1 | R
| 32 | Lower Warning 1 |  | 1 | R
|  | … |  |  | R
| 47 | Lower Warning 16 |  | 1 | R
| 48 | Lower Critical 1 |  | 1 | R
|  | … |  |  | R
| 63 | Lower Critical 16 |  | 1 | R
Displacement Power Factor
14D0 |  | Circuit Position Readings
| 0 | Mains A |  | 1 | R
| 1 | Mains B |  | 1 | R
| 2 | Mains C |  | 1 | R
| 3 | Circuit Position 1 |  | 1 | R
|  | … |  |  | R
| 3 + (c-1) | Circuit Position c |  | 1 | R
|  | … |  |  | R
15D0 |  | Circuit Position Events
| 0 | Upper Critical 1 |  | 1 | R
|  | … |  |  | R
| 15 | Upper Critical 16 |  | 1 | R
| 16 | Upper Warning 1 |  | 1 | R
|  | … |  |  | R
| 31 | Upper Warning 16 |  | 1 | R
| 32 | Lower Warning 1 |  | 1 | R
|  | … |  |  | R
| 47 | Lower Warning 16 |  | 1 | R
| 48 | Lower Critical 1 |  | 1 | R
|  | … |  |  | R
| 63 | Lower Critical 16 |  | 1 | R
Phase Angle
1610 |  | Circuit Position Readings
| 0 | Mains A |  | 1 | R
| 1 | Mains B |  | 1 | R
| 2 | Mains C |  | 1 | R
| 3 | Circuit Position 1 |  | 1 | R
|  | … |  |  | R
| 3 + (c-1) | Circuit Position c |  | 1 | R
|  | … |  |  | R
1710 |  | Circuit Position Events
| 0 | Upper Critical 1 |  | 1 | R
|  | … |  |  | R
| 15 | Upper Critical 16 |  | 1 | R
| 16 | Upper Warning 1 |  | 1 | R
|  | … |  |  | R
| 31 | Upper Warning 16 |  | 1 | R
| 32 | Lower Warning 1 |  | 1 | R
|  | … |  |  | R
| 47 | Lower Warning 16 |  | 1 | R
| 48 | Lower Critical 1 |  | 1 | R
|  | … |  |  | R
| 63 | Lower Critical 16 |  | 1 | R
RMS Currents
1750 |  | Circuit Summary Readings
| 0 | Mains |  | 1 | R
| 1 | Circuit 1 |  | 1 | R
|  | … |  |  | R
| c | Circuit c |  | 1 | R
|  | … |  |  | R
1850 |  | Circuit Summary Events
| 0 | Upper Critical 1 |  | 1 | R
|  | … |  |  | R
| 15 | Upper Critical 16 |  | 1 | R
| 16 | Upper Warning 1 |  | 1 | R
|  | … |  |  | R
| 31 | Upper Warning 16 |  | 1 | R
| 32 | Lower Warning 1 |  | 1 | R
|  | … |  |  | R
| 47 | Lower Warning 16 |  | 1 | R
| 48 | Lower Critical 1 |  | 1 | R
|  | … |  |  | R
| 63 | Lower Critical 16 |  | 1 | R
1890 |  | Circuit Position Readings
| 0 | Mains A |  | 1 | R
| 1 | Mains B |  | 1 | R
| 2 | Mains C |  | 1 | R
| 3 | Circuit Position 1 |  | 1 | R
|  | … |  |  | R
| 3 + (c-1) | Circuit Position c |  | 1 | R
|  | … |  |  | R
1990 |  | Circuit Position Events
| 0 | Upper Critical 1 |  | 1 | R
|  | … |  |  | R
| 15 | Upper Critical 16 |  | 1 | R
| 16 | Upper Warning 1 |  | 1 | R
|  | … |  |  | R
| 31 | Upper Warning 16 |  | 1 | R
| 32 | Lower Warning 1 |  | 1 | R
|  | … |  |  | R
| 47 | Lower Warning 16 |  | 1 | R
| 48 | Lower Critical 1 |  | 1 | R
|  | … |  |  | R
| 63 | Lower Critical 16 |  | 1 | R
Neutral Currents
19D0 |  | Circuit Position Readings
| 0 | Mains |  | 1 | R
|  | … |  |  | R
| 255 |  |  | 1 | R
1AD0 |  | Circuit Position Events |  |  | R
| 0 | Upper Critical 1 |  | 1 | R
|  | … |  |  | R
| 15 | Upper Critical 16 |  | 1 | R
| 16 | Upper Warning 1 |  | 1 | R
|  | … |  |  | R
| 31 | Upper Warning 16 |  | 1 | R
| 32 | Lower Warning 1 |  | 1 | R
|  | … |  |  | R
| 47 | Lower Warning 16 |  | 1 | R
| 48 | Lower Critical 1 |  | 1 | R
|  | … |  |  | R
| 63 | Lower Critical 16 |  | 1 | R
P.E. Currents
1B10 |  | Circuit Position Readings
| 0 | Mains |  | 1 | R
|  | … |  |  | R
| 255 |  |  | 1 | R
1C10 |  | Circuit Position Events
| 0 | Upper Critical 1 |  | 1 | R
|  | … |  |  | R
| 15 | Upper Critical 16 |  | 1 | R
| 16 | Upper Warning 1 |  | 1 | R
|  | … |  |  | R
| 31 | Upper Warning 16 |  | 1 | R
| 32 | Lower Warning 1 |  | 1 | R
|  | … |  |  | R
| 47 | Lower Warning 16 |  | 1 | R
| 48 | Lower Critical 1 |  | 1 | R
|  | … |  |  | R
| 63 | Lower Critical 16 |  | 1 | R
Active Energy (absolute)
1C50 |  | Circuit Summary Readings
| 0 | Mains |  | 4 | R
| 4 | Circuit 1 |  | 4 | R
|  | … |  |  | R
| c*4 | Circuit c |  | 4 | R
|  | … |  |  | R
2050 |  | Circuit Position Readings
| 0 | Mains A |  | 4 | R
| 4 | Mains B |  | 4 | R
| 8 | Mains C |  | 4 | R
| 12 | Circuit Position 1 |  | 4 | R
|  | … |  |  | R
| 12 + (c-1) * 4 | Circuit Position c |  | 4 | R
|  | … |  |  | R
Active Power (absolute)
2450 |  | Circuit Summary Readings
| 0 | Mains |  | 2 | R
| 2 | Circuit 1 |  | 2 | R
|  | … |  |  | R
| c*2 | Circuit c |  | 2 | R
|  | … |  |  | R
2650 |  | Circuit Position Readings
| 0 | Mains A |  | 2 | R
| 2 | Mains B |  | 2 | R
| 4 | Mains C |  | 2 | R
| 6 | Circuit Position 1 |  | 2 | R
|  | … |  |  | R
| 6 + (c-1) * 2 | Circuit Position c |  | 2 | R
|  | … |  |  | R
Reactive Power (absolute)
2850 |  | Circuit Summary Readings
| 0 | Mains |  | 2 | R
| 2 | Circuit 1 |  | 2 | R
|  | … |  |  | R
| c*2 | Circuit c |  | 2 | R
|  | … |  |  | R
2A50 |  | Circuit Position Readings
| 0 | Mains A |  | 2 | R
| 2 | Mains B |  | 2 | R
| 4 | Mains C |  | 2 | R
| 6 | Circuit Position 1 |  | 2 | R
|  | … |  |  | R
| 6 + (c-1) * 2 | Circuit Position c |  | 2 | R
|  | … |  |  | R
Apparent Power (absolute)
2C50 |  | Circuit Position Readings
| 0 | Mains A |  | 2 | R
| 2 | Mains B |  | 2 | R
| 4 | Mains C |  | 2 | R
| 6 | Circuit Position 1 |  | 2 | R
|  | … |  |  | R
| 6 + (c-1) * 2 | Circuit Position c |  | 2 | R
|  | … |  |  | R
RMS Currents (absolute)
2E50 |  | Circuit Summary Readings
| 0 | Mains |  | 2 | R
| 2 | Circuit 1 |  | 2 | R
|  | … |  |  | R
| c*2 | Circuit c |  | 2 | R
|  | … |  |  | R
3050 |  | Circuit Position Readings
| 0 | Mains A |  | 2 | R
| 2 | Mains B |  | 2 | R
| 4 | Mains C |  | 2 | R
| 6 | Circuit Position 1 |  | 2 | R
|  | … |  |  | R
| 6 + (c-1)* 2 | Circuit Position c |  | 2 | R
|  | … |  |  | R
Neutral Currents (absolute)
3250 |  | Circuit Position Readings
| 0 | Mains |  | 2 | R
|  | … |  |  | R
P.E. Currents (absolute)
3450 |  | Circuit Position Readings
| 0 | Mains |  | 2 | R
|  | … |  |  | R